Annex C

Technical Possibilities for Voltage and Reactive Power Control

There are mainly two options for voltage and reactive power control:

- Static Voltage Control

- Dynamic Voltage Control

Static Voltage Control

- Example: fixed power factor (cosφ = 0.95 lagging)

- Once set, it never changes, no matter what happens to grid voltage or frequency.

- Very simple, not “dynamic”.

Dynamic Voltage Control

It means the inverter automatically adjusts its active (P) or reactive (Q) power output  in response to changes in the grid voltage at the PCC.

- If grid voltage rises too high the inverter will absorb reactive power (inductive behavior).

- If grid voltage drops too low the inverter will inject reactive power (capacitive behavior).

This keeps the local voltage closer to nominal (e.g. 230/400 V).

Why it is needed

- In grids with lots of PV, local voltage can fluctuate as solar generation changes.

- Dynamic voltage control helps stabilize grid voltage without a need of mechanical equipment (like tap changers or capacitor banks).

- It is mandatory in most modern grid codes (Europe: ENTSO-E, Germany: EN 50549, VDE-AR-N 4105, UK G99, Australia AS4777, etc.).

How it works

Inverter firmware uses a for example Volt-Var (Q(U)) characteristic:

- Voltage at PCC is continuously measured.

- The inverter adjusts its reactive power (Q) according to a predefined curve:

- Inject Q (capacitive, supports low V),

- Absorb Q (inductive, reduces high V),

This is dynamic, i.e. real-time and automatic, not a fixed power factor. So when datasheets mention dynamic voltage control, Volt-Var control, or adjustable cosφ, or name of standards, which support this ability, they mean exactly this function.

In case of Hybrid Inverters there are follow features:

1. Grid-Forming

- A grid-forming inverter behaves like a voltage source (like a synchronous generator).

- It can create its own stable voltage and frequency reference, even if the main grid is absent (e.g. in islanded or micro grid operation).

- Opposite: grid-following inverters act like current sources and need the grid’s voltage/frequency to synchronize.

2. Droop Control

- Droop control is a control method supported by synchronous machines.

- It defines how the inverter adjusts its power output when voltage or frequency changes, to share load with other units without direct communication.

- Two main types:

  - P(f) droop: Active power and frequency. If frequency falls inverter injects more active power.

  - Q(V) droop: Reactive power and voltage. If voltage rises inverter absorbs reactive power; if voltage drops injects reactive power.

3. Grid-Forming and Droop Control

- A grid-forming inverter with droop control establishes voltage and frequency and uses droop laws to share load with other sources (inverters, generators, batteries).

- This allows multiple inverters to operate in parallel, automatically balancing power without a need of fast communication links.

4. Why It important

- In micro grids / hybrid systems: ensures stable islanded operation.

- For grid-support: can provide inertia-like response, voltage regulation, and black start.

- For renewables: allows solar + storage inverters to imitate generator behavior.

Dynamic voltage control curves

- The inverter continuously measures grid voltage (U) and frequency (f).

- Then it adjusts its output using control curves:

- Q(U): Volt-Var (reactive power vs. voltage)

  - Injects/absorbs Q depending on U.

- P(U): Volt-Watt (active power vs. voltage)

  - Reduces P if voltage gets too high.

- cosφ(P): Power factor vs. active power

  - Changes PF depending on load/generation.

- Q(P): Reactive power vs. active power

  - Changes Q depending on P output.

- Grid-forming droop control (in hybrid)

  - Grid-forming droop control means an inverter sets grid voltage and frequency (like a generator) and adjusts active/reactive power according to droop curves, enabling stable load sharing and autonomous operation in grids or microgrids.

  - Inverter sets voltage and frequency and adapts them dynamically depending on load sharing. Grid-forming droop control is a control strategy that lets a hybrid inverter create its own grid (voltage + frequency) while automatically sharing power with other sources through P(f) and Q(V) droop characteristics - just like traditional generators in micro grids. So when datasheets say “dynamic voltage control”, they mean specifically Q(U) mode - reactive power automatically controlled by voltage changes. But in practice, modern inverters support all four curves (Q(U), P(U), cos(P), Q(P)), and if hybrid then also droop control.

In summary:

- Fixed PF is static voltage control.

- Q(U), P(U), cos (P), Q(P), droop is dynamic voltage control.

No Voltage Control

Some older inverter models lack the ability to perform either static or dynamic voltage control. In this case, the PF of such inverters tends toward cosφ = 1, but more often, cosφ < 1 (inductive behavior), as the inverters require some reactive power for its operation.

Modern inverters have P(f) control and regulation abilities:

- P(f) means Active Power as a function of Frequency.

- It is also called frequency-dependent active power control or frequency-watt control.

- Inverters with P(f) capability automatically adjust their active power output depending on the grid frequency.

Why it is needed

- The electrical grid must always keep frequency stable (50 Hz).

- If the frequency rises: it means there is too much generation compared to consumption.

- If the frequency drops: it means there is too much consumption compared to generation.

Traditionally, big power plants provided with this stabilizing function.

How it works (with curve)

Imagine a solar inverter connected to a 50 Hz grid:

- 50 Hz (nominal): inverter produces 100% active power (Pmax).

- 50.2 Hz: inverter starts reducing active power.

- 51.5 Hz: inverter might reduce to 0% output (depending on country grid code).

- The slope is defined by standards (e.g., Germany VDE-AR-N 4105, UK G99, etc.).

- The deadband (no action zone, like 49.8–50.2 Hz) avoids unnecessary power swings.

In simple words:

- P(f) control - inverter helps the grid by lowering its active power when frequency is too high.

- It is a type of grid-support / ancillary service built into all certified modern inverters.

When the inverter is producing for example 10 kW at 50 Hz, and the grid frequency rises to 50.6 Hz, the inverter might reduce to ~7 kW automatically, following the P(f) curve programmed in its settings.